|  | Nursing Service Guidelines for Hemodialysis |  |
| --- | --- | --- |

| Title: | Scheduled Water/Dialysate Culture and LAL Specimens |
| --- | --- |
| Responsibility: | Hemodialysis RN/Biomed |
| Equipment: | Sterile 30ml syringe remove Biomed will revise this one. Sterile 10ml syringe remove Chloraprep swabs Specimen Container LAL test tube Spectra Lab specimen slip and shipping container |

| Procedure | Point of Emphasis |
| --- | --- |
| Dialysate Specimen |  |
| - Culture/LAL schedule list is located in the “Hemo Log” book. Set up Dialysis machine to be in conductivity. Record samples taken in the Hemo log book. | All machines are done on a rotating scheduled basis. |
| - Cleanse sampling port on venous line of Hanson with Chloraprep swab in a circular motion starting at the center and wiping outward. | To cleanse bacteria off of port to prevent contamination of specimen. |
| - Withdraw Allow 30 ml of dialysate to flow into a container. and discard. | To draw off any contaminants in the sample port. |
| - Withdraw 10 ml of dialysate for specimen and place in sterile specimen cup or LAL specimen test tube. Clean catch dialysate sample into sterile container. Transfer samples to test tubes. | Maintain sterility to prevent contamination of specimen. |
| - Complete Spectra Lab form, label specimen and prepare to ship | Specify machine #, if sample is dialysate or R/O water and if specimen for culture or LAL. Specimens that cannot be shipped immediately will need to be refrigerated. |
| Water Specimen |  |
| - Culture/LAL schedule list is located in the “Hemo Log” book for portable RO system. | All stations portables are done on a rotating scheduled basis. |
| - Run water for 3 min. at a slow to mod. rate. In soiled and clean room, use portable hose to run water to drain and disconnect hose after the 3 min. flush.Verify the portable RO unit is making product water. | To flush outlet of contaminants in the water system. |
| - Cleanse water outlet with Chloraprep swab. For R/O (reverse osmosis) units, soak dual line hose connection in solution of 10 parts water and 1 part bleach for 5 minutes | To cleanse bacteria off of outlet to prevent contamina-tion of specimen. Rinse dual line hose connection and connector at end of dual line hose with R/O water after bleach water soak to remove residual bleach. |
| - Turn on water slowly and obtain a CCMS sample of R/O water (at least 10ml). For R/O unit, allow water to run for 15 minutes prior to obtaining CCMS sample from dual hose line (with dual hose connector connected). Allow 30ml or more water to flow into a bucket. Clean catch water sample into a sterile container. Transfer samples to test tubes. | Maintain sterility. |
| - Complete Spectra Lab form, label specimen and prepare to ship. | Be sure to specify station location and if specimen is R/O water or LAL. Specimens that cannot be shipped immediately will need to be refrigerated. . |

Revised by:	Tom Shaw, Biomedical Engineering

Resource Person:

Reviewed by:	Alexa McNamee, RN

Approved:	3/96

Reviewed:	5/99, 7/02, 7/03, 7/05, 1/07, 4/08, 2/11, 5/14, 6/18, 4/21

Revised:	 5/27/2011, 6/2015, 5/2024

Reviewed by Policy & Standard Committee, 5/11, 6/18, 4/21, 5/24

References:	AMI Standards 2017